## Sheet1
Q 1. | Q 2. | Q 3. | Q 4.
BACKUP
| How to charge? | Feed in? | PV Type? | Suggested configuration
| Always (PV + Grid) | Yes | AC-Coupled | PV Inverter Support Assistant
|  |  | DC-Coupled | Hub-1 Assistant "Keep batteries charged"
|  | No | AC-Coupled | Don't do this, use a MPPT Solar Charge Controller instead. A PV Inverter will want to feed back, and trying to prevent that only complicates the install.
|  |  | DC-Coupled | Hub-1 Assistant "Connected to mains, no feedback"
| PV Only | Yes | AC-Coupled | Hub-4 Assistant. Set the Minimum state of charge in the CCGX to 100%
|  |  | DC-Coupled | Hub-1 Assistant "Keep batteries charged". Charger tab op 0A to prevent charging from grid (sustain will overrule the max charge current)
|  | No | AC-Coupled | Consider using an MPPT instead. And if not possible, use Hub-2 Assistant "Connect to AC In when available, keep batteries charged", and enable the prevent feedback setting.
|  |  | DC-Coupled | Hub-1 Assistant "Connected to mains, no feedback". Charger tab op 0A to prevent charging from grid
| Genset | No | AC-Coupled | All Multi settings to default and use the PV Inverter Assistant. Possible connect PV on AC OUT 2 and use an Assistant to disconnect it when the genset is running
|  |  | DC-Coupled | Option 1) All default
Option 2) Hub-1 Assistant "Connected to mains, no feedback". Advantage over option 1 is that PV power will be used when available, instead powering all loads with genset
SELF-CONSUMPTION
| How to charge? | Feed in? | PV Type? | Suggested configuration
| PV Only | Yes | AC-Coupled | Hub-4 Assistant
|  |  | DC-Coupled | Hub-1 Assistant "Connected to mains, feedback"
|  | No | AC-Coupled | Consider using an MPPT instead. And if not possible, use the Hub-2 Assistant "Day/night mode, prevent feedback"
|  |  | DC-Coupled | Option 1) Hub-4 Assistant <- recommended, dynamic cutoff, much simpler etc.
Option 2) Hub-1 Assistant
SELF-CONSUMPTION WITH BATTERY RESERVE FOR GRID FAILURES
| How to charge? | Feed in? | PV Type? | Suggested configuration
| PV | Yes | AC-Coupled | Hub-4 Assistant. Configure the Minimum state of charge in the CCGX
|  |  | DC-Coupled | Not possible. Best is to use the no-feedin alternative, or use Hub-1, but it does not allow setting an SOC. Hub-1 works only on Battery Voltage.
|  | No | AC-Coupled | Consider using an MPPT instead. And if not possible, use the Hub-2 Assistant. Enable Prevent feedback. Configure the minimal SOC in the Battery Empty Levels page of the Hub-2 assistant.
|  |  | DC-Coupled | Hub-4 Assistant. Configure the Minimum state of charge in the CCGX
OFF-GRID
| How to charge? | Feed in?
| When genset runs, max pwr | n.a. | AC-Coupled | PV Inverter Support Assistant
| Otherwise PV |  | DC-Coupled | MPPT + Multi, no Assistants or other config needed
INTENTIONAL ISLANDING
| How to charge? | Feed in?
|  | not applicable | AC-Coupled | PV Inverter Assistant + General Flag and Generator Start/Stop
|  | not applicable | DC-Coupled | Virtual switch - Dedicated ignore AC Input